## How to fill
Solar91 O&M — Plant side Preventive Maintenance plan
Only Plant side equipment goes in this file. GSS side equipment is rejected on upload — use the GSS side template for it. One row = one PM job.
Column / topic | What to enter
Order of work | The portal does the Plant side equipment in this order: 1. Inverter (Inverter) — cycle days 1–7 2. ACCB (ACCB Panel) — cycle days 8–9 3. VCB (VCB Panel) — cycle days 10–11 4. IDT Transformer (Transformer) — cycle days 12–13 5. Aux. Transformer + ACDB (Aux. Transformer, ACDB) — cycle days 14–15 6. 4 Pole (4 Pole) — cycle days 16–17 7. Earth pit (Earthing) — cycle days 18–19 8. Miscellaneous (Street Light, ERT, … as one Miscellaneous job; any other equipment type not listed here) — cycle days 20–22 9. Transmission line (Transmission line) — cycle days 23–24 The GSS side (VCB, 4 Pole, Transmission line) follows after the plant side is finished.
Date | There is no date column. Choose the cycle start date (day 1) in the portal when you upload: Preventive Maintenance → Import CSV / Excel. Every equipment's dates follow from the order above.
No overlap | If earlier work at a plant takes longer than its days (for example 20 inverters at 2 a day = 10 days), the next equipment starts the day after it finishes and everything after it moves too. The portal shows the final dates before anything is saved.
Equipment type | Pick from the dropdown. It lists only Plant side equipment.
Plant(s) | Plant name or code exactly as in the portal; several plants separated by commas, or All plants. Rows without a plant are saved as PM job templates only (no tasks).
Task - what to do | Short name of the job. Keep Plant side and GSS side task names different.
Frequency - when | Monthly for the 30-day cycle (each unit comes back on the same cycle day next month).
Assignee(s) | O&M team member(s) with the Assignee role, separated by commas.
Safety needed | — (none), PTW required, LOTO required, or PTW + LOTO required.
Est. time (hours) | Approximate hours per unit, as a number.
How to do it | Steps / checklist in plain words.
No. of units | Optional. How many units the plant has. Blank = the plant's Unit configuration or Equipment Register. ACCB Panel (ACCB-1 + ACCB-2), Aux. Transformer, ACDB and Miscellaneous are always one job per plant.
Units per day | Optional. Most units done in one day. Blank = spread the units over the equipment's cycle days.
Remarks | Optional. Added to the log of every task the row creates. For Miscellaneous, list the items the job covers (pre-filled: Street Light, ERT — remove or add items).
Order in PM cycle | For information only; the portal ignores this column.

## PM Tasks
Equipment type | Plant(s) | Task - what to do | Frequency - when | Assignee(s) | Safety needed | Est. time (hours) | How to do it | No. of units | Units per day | Remarks | Order in PM cycle (info only)
Inverter |  | Inverter preventive maintenance | Monthly |  | PTW + LOTO required | 2 | 1. Isolate. 2. Clean fans and filters. 3. Check DC / AC terminal torque. 4. Review alarms. 5. Record readings. |  |  |  | Plant side step 1 · cycle days 1–7
ACCB Panel |  | ACCB panel PM (ACCB-1 + ACCB-2, one job) | Monthly |  | PTW + LOTO required | 2 | 1. Isolate. 2. Breaker operation check. 3. Busbar / terminal thermal scan. 4. Cable lugs. 5. Panel cleaning. Do ACCB-1 and ACCB-2 in the same job. | 1 |  |  | Plant side step 2 · cycle days 8–9
VCB Panel |  | VCB panel PM (plant side) | Monthly |  | PTW + LOTO required | 3 | 1. Breaker mechanical operation. 2. Contacts / terminals. 3. Relay & trip-circuit test. 4. Interlocks. |  |  |  | Plant side step 3 · cycle days 10–11
Transformer |  | IDT transformer PM | Monthly |  | PTW + LOTO required | 3 | 1. Oil level / leakage. 2. Bushings & breather. 3. Temperature / protection checks. 4. Earthing & terminals. |  |  |  | Plant side step 4 · cycle days 12–13
Aux. Transformer |  | Aux. transformer PM | Monthly |  | PTW + LOTO required | 2 | 1. Oil / enclosure. 2. Bushings & cables. 3. Voltage / current reading. 4. Earthing continuity. | 1 |  |  | Plant side step 5 · cycle days 14–15
ACDB |  | ACDB panel PM | Monthly |  | PTW + LOTO required | 1 | 1. Isolate. 2. Incomer / outgoing breaker operation. 3. Busbar / terminal thermal scan. 4. Cable lugs. 5. Panel cleaning. | 1 |  |  | Plant side step 5 · cycle days 14–15
4 Pole |  | 4 Pole structure PM (plant side) | Monthly |  | PTW required | 2 | 1. Structure & foundation. 2. Insulators / jumpers. 3. Earthing connection. 4. Hardware tightening. |  |  |  | Plant side step 6 · cycle days 16–17
Earthing |  | Earth pit maintenance | Monthly |  | — | 2 | 1. Earth-pit condition. 2. Resistance measurement. 3. Connection tightening. 4. Watering / treatment. |  |  |  | Plant side step 7 · cycle days 18–19
Miscellaneous |  | Miscellaneous PM | Monthly |  | — | 2 | Check each item named in Remarks (Street Light, ERT, …). All in one job. | 1 |  | Street Light, ERT | Plant side step 8 · cycle days 20–22
Transmission line |  | Transmission line patrol & PM (plant side) | Monthly |  | PTW required | 4 | 1. Line patrol. 2. Conductor / sag. 3. Insulators / jumpers. 4. Poles / towers. 5. Vegetation & ROW. |  |  |  | Plant side step 9 · cycle days 23–24

## Lists
Equipment types | Frequency | Safety
Inverter | Daily | —
ACCB Panel | Weekly | PTW required
VCB Panel | Monthly | LOTO required
Transformer | Quarterly | PTW + LOTO required
Aux. Transformer | Half-yearly
ACDB | Annual
4 Pole
Earthing
Miscellaneous
Transmission line
Piling and Foundation
WMS
OLTC(RTCC)
RMS
ABT meters
LA
CCTV
Boundary wall
Water pipe line
Vegetation
Street Light
BIKE
Other

## Task ideas
Equipment type | Common checks
Inverter | Fan / filter cleaning • Alarm & fault-history review • DC / AC terminal torque check • Insulation resistance reading • Firmware / communication health
ACCB Panel | Breaker operation check • Busbar / terminal thermal scan • Protection & metering check • Cable gland / lug inspection • Panel cleaning
VCB Panel | Breaker mechanical operation • Contact / terminal inspection • Relay & trip-circuit test • Spring charging mechanism • Interlock / indication check
Transformer | Oil level / leakage inspection • BDV / moisture / DGA test as scheduled • Bushing & breather inspection • Protection / temperature checks • Earthing & terminal tightening
Aux. Transformer | Oil / enclosure inspection • Bushing & cable check • Voltage / current reading • Protection check • Earthing continuity
ACDB | Incomer / outgoing breaker operation, busbar / terminal thermal scan, cable lugs, panel cleaning
4 Pole | Structure and foundation inspection • Insulator / jumper inspection • Earthing connection check • Hardware tightening • Hotspot / corona inspection
Earthing | Earth-pit condition • Resistance measurement • Connection tightening • Corrosion check • Watering / treatment where applicable
Miscellaneous | Street Light, ERT and other small items — one job per plant; list them in Remarks
Transmission line | Line patrol • Conductor / sag inspection • Insulator / jumper inspection • Tower / pole / foundation inspection • Vegetation & ROW clearance
Piling and Foundation | Foundation inspection • Pile condition check • Settlement / alignment check • Crack / damage inspection • Corrective action review
WMS | Sensor cleaning • Irradiance / temperature sensor validation • Communication check • Calibration comparison • Mounting / cable inspection
OLTC(RTCC) | Tap-changer position / indication check • Auto-manual mode operation • Control wiring and relay inspection • Communication / SCADA signal check • Panel cleaning
RMS | Communication availability • Data-gap / timestamp review • Router / modem / network check • Power / UPS backup check • Portal value validation
ABT meters | Meter reading validation • RTC / time sync • Seal / wiring inspection • Communication availability • Energy-data reconciliation
LA | Visual condition • Counter reading • Connection tightening • Earth continuity • Post-lightning inspection
CCTV | Camera feed check • Lens / housing cleaning • NVR / DVR recording & storage check • UPS / network check • Coverage / night-vision verification
Boundary wall | Wall / fencing patrol • Crack / settlement inspection • Gate / access check • Breach / damage repair review • Drainage / erosion observation
Water pipe line | Leak / blockage inspection • Pump / valve operation • Pressure / flow observation • Joint / support inspection • Repair / flushing requirement
Vegetation | Grass / weed cutting • Module shading check • Fire-risk / dry biomass removal • ROW / access clearing • Waste disposal
Street Light | Fixture operation • Timer / controller check • Cable / pole inspection • Earthing check • Night operation verification
BIKE | Bike Not Starting • Accident / Body Damage • Functional check • Engine Problem • Corrective action review
Other | Define task-specific checklist • Capture measurements / readings • Attach photo / video evidence • Record remarks / anomalies • Escalate problem to Issue if required